## Overview of Placement Rules
Overview of Placement Rules
Project
● 1 or more Systems
System
● Contains 1 or more Panels
● Panel with a CPU (1 Max per System) - can have a system without a CPU Panel
● Basic
● Redundant
● NDU
● NDU with Voice
● Non-CPU panel (no limit)
● Transponder
● Remote Annunciator
● Max 118 addressed modules (all the panels combined)
|  | ● In NDU with Voice Panels, the "duplicate" modules between bay 1 and bay 2 have the same addresses. (i.e. both Master ESPS, etc) |  |  |  |  | x x
● All Panels must contain the same type:
● Audio (Analog/Digital)
● AC Voltage (120/220V/230V/240V)
● Assigned a unique “File Number”
|  | ● Once a system is built, an extract text file, with the extention "xdb" will need to be created so that the layout can be imported into the 4100ES programmer (this is a requirement of the project) |  |  |  |  | x x
Panel
● 1 to 8 Cabinets (containing a total of 1 to 24 bays)
x x x x x x x
Included automatically with each Panel
● Basic - Display, CPU module, Master ESPS (power supply), Bay Chassis
Internal Panel Bay Space Modules Picture Outer Door Space
x x x x x x x
|  |  | ● Redundant - 1 or 2 Display(s), 2 CPU module, 2 Master SPS, 2 Bay Chassis, 24-point I/O modules, CPU Switcher module |  |  |  | x x
● Special module placment
● CPU module (Legacy module) - mounts in Bay 1 Slot 2 and Bay 2 Slot 4
● Master SPS (Legacy power supply) - mounts in Block EFGH
● 24-point I/O module (Legacy module) - Mounts Bay 1 Slot 4
● CPU Switcher module (Legacy module) - mounts in Box 1 Bay 1 Slot 2
x x x x x x x x x x x x x x
● NDU - Display, CPU Module, Master ESPS (power supply), Bay Chassis, Network module
x x x x x x x
● NDU with Voice - Display, 2 CPU modules, 2 Master ESPS (Power supply), 2 Bay Chassis, 2 Network modules
x x x x x x x x x x x x x x
● Transponder - Transponder Interface module, Bay Chassis
x x x x x x x
● Remote Annunciator - Transponder Interface module, Bay Chassis, 0 or 1 Display
x x x x x x x
Special Considerations
|  |  | ● Redundant - Bay 1 has no open slots/blocks availbalbe for optional modules (except a Side-mounted SDACT) and Bay 2 has not open slots/blocks available for optional modules (except LED/Switchs and LED/Switch controllers) |  |  |  | x x
● NDU - Limited modules available/placement
● NDU with Voice - Bay 1 is the NDU "panel" and Bay 2 is a Basic "panel" without a display.
● Transponder - requires at least 1 power supply and no Annunciation modules are allowed
● Remote Annunciator - Only for annunciation
● Three different types
● Remote Annunciator - requires at least 1 power supply
● Basic Remote Annunciator - power is supplied from the host panel
|  |  | ● Remote Annuciator with Incident Commander - user specifies the Transponder Interface module, requires at least 1 power supply and Bay 2 is dedicated to an Incident Commander. |  |  |  | x x
Cabinet
● 1 to 3 Bays per cabinet - can mix and match as required by project/field requirements
|  |  |  | ● Glass or Solid Door - can mix and match as needed - though Transponders can only have Solid and Remote Annunciators can only have Glass |  |  | x x
● One cabinet enclosure or indicator pid required per a cabinet (depending on size, color and type)
● One Power Distribution Module required per a cabinet
● Max of 4 power supplies per a cabinet
Bay
[5 empty] | ● Bays are 10”x16”X7” Chassises that consists of a back plate, side rails (on the sort ends), and a door frame, hinged for easy access to the back plate and behind the door frame. |  | x x
[5 empty] | ● For layout and mounting purposes, bays are broken up into Slots (2” x 10”) or Blocks (4” x 5”) or a combination of either depending on the modules ordered. |  | x x
● 4 Planes – Back, Mezzanine, Behind the Door & Front of the Door
● The planes are interactive – placement in one plane can affect placement in others
● The Mezzanine and Behind the Door planes interfere with each other.
[5 empty] | ● Some modules take up more then one plane on their own, for example, both the Back and Mezzanine planes or the Behind the Door and Front of Door planes |  | x x
● Here are different ariel views of the planes
x x x x x x x x x x x x x x
[5 empty] | ● Bays are 10”x16”X7” Chassises that, for layout purposes, are broken up into Slots (2” x 10”) or Blocks (4” x 5”) or a combination of either depending on the modules ordered and the plane. |  | x x
[5 empty] | ● Modules can use either single slots/blocks (i.e. Slot 1 or Block B) or combinations of slots/blocks (i.e. Slot123 or BlockEFGH) |  | x x
● Slots/Blocks are not used on every plane
● Back plane uses Slots and Blocks
● Mezzanine plane uses Slots and Blocks (same as parent module)
● Behind Door plane uses Blocks
● Front of Door plane uses Slots
● Here a head on view of the bay split into Slots and Blocks
x x x x x x x x x x x x x x
● Bay Types
● Master Controller Bay contains the CPU
● Audio Controller Bay contains an Audio Controller or "Basic Audio with Microphone"
● Incident Commander bay is a space holding bay for a Incident Commander (ordered separately)
● Expansion Bay is all other bays
● Each expansion bay and Audio bay (without a Basic Audio with Microphone) requires a Chaissis
● Power is daisy-chained downward
Module
● Modules that mount in the Back Plane
● ES Modules – 4” x 5” or 4” x 10” flat boards
● Cannot mount next to a Legacy module - must keep at least a slot between them
[6 empty] | ● Basic Audio with Microphone - Consist of an Audio Controller, Microphone and Chassis - See individual components for placement | x x
[6 empty] | ● Audio Controller |  | 1311
● Worst Case Load
● Standby Load = 0.0850, Alarm Load = 0.0850
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0850
● Needs 1 Address
● Mounts in Block AB
● Two types: Analog and Digital
[6 empty] | ● In a Basic Panel, mounts in Bay 2 (except if an Incident Commander is ordered, then mounts in Cab 1 Bay 3 or Cab 2 Bay 2) | x x
[6 empty] | ● In a Redundent Panel, mounts in Bay 3 (except if an Incident Commander is ordered, then mounts in Cab 1 Bay 3 or Cab 2 Bay 2) | x x
[6 empty] | ● In a NDU with Voice, mounts in Bay 2 - The second bay of the NDU with Voice is moved to Bay 3 (though this bay powers the Audio Controller bay) - (except if an Incident Commander is ordered, then mounts in Cab 2 Bay 2) | x x
● Mounts on the back plate only (not on a power supply)
[6 empty] | ● Auxiliary Audio Input Board |  | 1240
● Worst Case Load
● Standby Load = 0.0100, Alarm Load = 0.0500
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0500
● Needs same address as the Audio Controller
● Max 2 per Audio Controller
● Mounts in Block A (for 1st one) or Block B (for 2nd one)
● Must in same bay as Audio Controller
● Mounts on the back plate only (not on a power supply)
[6 empty] | ● NAC module |  | 5450
● Worst Case Load
● Standby Load = 0.0660, Alarm Load = 0.0660
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0660
● Needs 1 Address
● Mounts in a single block (Block A, Block B, Block C, Block D, Block E, Block F, Block G, Block H)
[6 empty] | ● Each Basic and NDU with Voice panel must either have at least one NAC module or one IDNAC module. | x x
[6 empty] | ● Mounts either on top of a power supply (9A available) or in the same bay as a power supply (6A available) | x x
● Supplies 3 Class A/B TrueAlert Non-Addressable NACs
[6 empty] | ● IDNAC module |  | 5451
● Worst Case Load
● Standby Load = 0.1040, Alarm Load = 0.1650
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.1650
● Needs 1 Address
● Mounts in two blocks (Block AB, Block CD, Block EF, Block GH)
[6 empty] | ● Each Basic and NDU with Voice panel must either have at least one NAC module or one IDNAC module. | x x
● Mounts top of a power supply (9A available)
● Supplies 3 Class B IDNACs
[6 empty] | ● Expansion Phone module |  | 1272
● Worst Case Load
● Standby Load = 0.0800, Alarm Load = 0.1400
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.1400
● Needs 1 Address
● Mounts in a single block (Block A, Block B, Block C, Block D, Block E, Block F, Block G, Block H)
● Cannot mount in CPU bay
● Mounts on the back plate only (not on a power supply)
[6 empty] | ● Master Controller IDNet2 module |  | 3117
● Worst Case Load
● Standby Load = 0.2500, Alarm Load = 0.3500
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.3500
● Needs 1 Address
● Must mount in Box 1 Bay 1 Block E
● Mounts either on top of a power supply or on the back plate
[6 empty] | ● Master Controller MXLoop module |  | 3118
● Worst Case Load
● Standby Load = 1.2350, Alarm Load = 1.2350
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0350
● Needs 1 Address
● Must mount in Box 1 Bay 1 Block AB
● Mounts either on top of a power supply or on the back plate
[6 empty] | ● IDNet2 module |  | 3109
● Worst Case Load
● Standby Load = 0.2500, Alarm Load = 0.3500
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.3500
● Needs 1 Address
● Mounts in a single block (Block A, Block B, Block C, Block D, Block E, Block F, Block G, Block H)
● Mounts either on top of a power supply or on the back plate
[6 empty] | ● 8 Point Zone/Relay module |  | 5013
● Worst Case Load
● Standby Load = 0.1150, Alarm Load = 0.2410
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.2410
● Must mount in the same bay as the 25V Regulator module
● Max 5 per 25V Regulator module
● For each one connected to the 25V Regulator module, a 25V Regulator harness is needed
[6 empty] | ● Network Audio Riser Controller module |  | 623
● Worst Case Load
● Standby Load = 0.0110, Alarm Load = 0.0110
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0110
● 1 Max
● Cannot mount in CPU bay
● Mounts in second or thrid Expansion bay, in Block A (preferred) or Block C
● Required an Audio Riser module (Analog or Digital)
[6 empty] | ● Audio Riser module |  | 622
● Worst Case Load
● Standby Load = 0.0700, Alarm Load = 0.0700
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0700
● Analog Audio Riser module
● 1 Max
[6 empty] | ● Must mount in Block B or Block D (directly "below" the Network Audio Riser Controller module) | x x
● Digital Audio Riser module
● No Max (1 Max as a Network Audio Riser Controller module)
● If used a Network Audio Riser Controller module
[6 empty] | ● Must mount in Block B or Block D (directly "below" the Network Audio Riser Controller module, if ordered) | x x
● If used a Non-Alarm Audio Input module
● One per bay
[6 empty] | ● Mounts in a single block (Block A, Block B, Block C, Block D, Block E, Block F, Block G, Block H) | x x
● Cannot mount in same bay as an Audio LED/Switch module
● Invalid in a panel with an Analog Audio Controller
[6 empty] | ● 25V Regulator module |  | 5130
● Worst Case Load
● Standby Load = 3.0000, Alarm Load = 4.9000
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0000
● Must mount in same bay as an ESPS power supply
[6 empty] | ● Mounts in CPU or expansion bay, Block A, Block B, Block C, Block D, Block E, Block F, Block G, Block H | x x
● Mounts on the back plate only (not on a power supply)
● Cannot mount behind Panel Mounted Printer, Phone Enclodure or Microphone
[6 empty] | ● MX Digital Loop module |  | 6077
● Worst Case Load
● Standby Load = 1.2350, Alarm Load = 1.2350
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0350
● Mounts in Block AB, Block CD, Block EF, Block GH
● Cannot mount behind a Panel Mounted Printer
[6 empty] | ● Requries a power supply in the same bay (except if mounted in Box 1 Bay2, when using the MX Loop Card Power Supply Harness) | x x
● Power Supplies (P/S)
● Needs 1 Address
[6 empty] | ● If more then 1 per a bay (max is 4), then each power supply MUST have a Fan Module mounted on it (this includes the power suuplies that are included with the panel). | x x
● There are 19 ES Modules that can mount on top of the power supply
● One 4 x 10 per a power supply
● Two 4 x 5 per a power supply
[6 empty] | ● ESPS |  | 5401
● Worst Case Load
● Standby Load = 0.0680, Alarm Load = 0.0770
● Card Power
● Card Power Available = 2.0000, Card Power Consumed = 0.0000
● 2V card power available
● Depending on different factors, the available power changes
● Basic/Base module (9.5V available)
● One per a bay
● Unless mounted with two Flex amps, see rule below, mounts in Block GH
● In same bay as Flex Amp(s) - see Amp rules
● With one Flex Amp, mounts in Block GH
● With two Flex Amps, mounts in Block CD
● IDNAC modules mounted on it (9.7V available)
● One per a bay
● All IDNAC modules MUST be mounted on a power supply
[6 empty] | ● Follows same rules as the "Basic/Base module" and "With Fan module", voltage doesn't change. | x x
● With Fan module (12.7V available)
● One per a bay
● Fan required if a Backup or ESXPS are in the same bay
● Mounts in Block GH
● Backup (N/A)
● One per a bay
● Must in same bay as an ESPS (to the left of the ESPS)
● Fan Module and Backup Harness are required
● All power supplies in the bay must have a Fan module
● Mounts in Block EF
● Used for Regulated 24V devices (5V available)
[6 empty] | ● Follows same rules as the "Basic/Base module", "IDNAC modules mounted on it" and "With Fan module", voltage doesn't change. | x x
[6 empty] | ● ESXPS |  | 5402
● Worst Case Load
● Standby Load = 0.0680, Alarm Load = 0.0770
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0000
● Does not supply card power
● Only supplies power to the modules placed on it
● Depending on different factors, the available power changes
● Basic/Base module (9.5V available)
● One per a bay
● Mounts in Block GH
● IDNAC modules mounted on it (9.7V available)
● One per a bay
● All IDNAC modules MUST be mounted on a power supply
[6 empty] | ● Follows same rules as the "Basic/Base module" and "With Fan module", voltage doesn't change. | x x
● With Fan module (12.7V available)
● Four per a bay
● Fan required ESPS or ESXPS are in the same bay
● Mounts right to left (Block Gh, Block Ed, Block CD, BlockAB)
● Used for Regulated 24V devices (5V available)
[6 empty] | ● Follows same rules as the "Basic/Base module", "IDNAC modules mounted on it" and "With Fan module", voltage doesn't change. | x x
● Amplifiers - uses Back amd Mezzanine planes
● Needs 1 Address
● Can only mount in an Audio Controller bay or Expansion bay
● If in CPU panel, required either an Audio Controller or Network Audio Riser Controller
[6 empty] | ● 100W |  | 1325
● Worst Case Load
● Standby Load = 0.4100, Alarm Load = 9.6000
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0000
● Mounts in Block EFGH
[6 empty] | ● 100W Backup |  | 1325
● Worst Case Load
● Standby Load = 0.4100, Alarm Load = 9.6000
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0000
● Mounts in Block ABCD
● Must mount in same bay as a 100W
[6 empty] | ● Flex Amp |  | 1312
● Worst Case Load
● Standby Load = 0.4250, Alarm Load = 5.6240
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0740
● Must mount in same bay as an ESPS power supply
● Different mounting requirements
● One amplifer paired with an ESPS
● Amplifier - Block EF
● ESPS - Block GH
● One amplifer paired with an ESPS with a backup ESPS
● Amplifier - Block CD
● Backup ESPS - Block EF
● ESPS - Block GH
● Two amplifiers paired with a ESPS
● Amplifier 1 - Block AB
● ESPS - Block CD
● Amplifier 2 - Block GH
● Block EF is reserved (must stay empty)
● The ESPS can only power the amps and nothing can be mounted on it
● Legacy Modules – 2” x 10” or 4” x 10” tall boards
● Cannot mount in an Audio Controller bay
● Cannot mount next to an ES module - must keep at least a slot between them
● Cannot mount behind 64/64 controller, Microphone, Phone enclodure or Panel Mounted Printer
● Mounts left to right
● In CPU bay, mounts in Slot 1, Slot 2
[6 empty] | ● In expansion bay, mounts in Slot 2, Slot 3, Slot 4, Slot 5, Slot 6, Slot 7, Slot 8, Slot 23, Slot 34, Slot 45, Slot 56, Slot 67, Slot 78 | x x
[6 empty] | ● Mapnet module |  | 3102
● Worst Case Load
● Standby Load = 0.4709, Alarm Load = 0.4909
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.4909
● In expansion bay, mounts in Slot 23, Slot 34, Slot 45, Slot 56, Slot 67, Slot 78
● Cannot mount in CPU bay
[6 empty] | ● CPU module |  | CPU
● Worst Case Load
● Standby Load = 0.1880, Alarm Load = 0.2000
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.2000
● Included with Basic, NDU and NDU with Voice panels
● Must mount in Slot 3
● Slot 4 can only be used for Network or RS232 modules
[6 empty] | ● Network module |  | 6078
● Worst Case Load
● Standby Load = 0.0460, Alarm Load = 0.0460
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0460
● Can be added to Basic and Redundant panels
● Included with NDU and NDU with Voice panels
● Must mount in Slot 4, next to the CPU module
● Requries 1 Network Media module minumium
● Max 2 Network Media modules per Network module
[6 empty] | ● RS232 Interface module |  | 6038
● Worst Case Load
● Standby Load = 0.1320, Alarm Load = 0.1320
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.1320
● Max 3
● If there is a Network module in the panel
● In CPU bay, mounts in Slot 1, Slot 2
● In expansion bay, mounts in Slot 2, Slot 3, Slot 4, Slot 5, Slot 6, Slot 7, Slot 8
● If there is no Network module, 1st one must place in Slot 4, next to the CPU module
● 1st one must place in Slot 4, next to the CPU module
● In CPU bay, mounts in Slot 1, Slot 2
● In expansion bay, mounts in Slot 2, Slot 3, Slot 4, Slot 5, Slot 6, Slot 7, Slot 8
[6 empty] | ● SDACT |  | 6052
● Worst Case Load
● Standby Load = 0.0300, Alarm Load = 0.0400
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0400
● Max 2
● Legacy style module
● In CPU bay, mounts in Slot 1, Slot 2 (prefered)
● In expansion bay, mounts in Slot 2, Slot 3, Slot 4, Slot 5, Slot 6, Slot 7, Slot 8
● Side Mount style module
● Mounts on left side end support in the CPU bay
● Slot 1 is not available
● Block A, Block B and Block AB are available
● Modules that mount in the Mezzanine Plane
● Flat boards that mount on other modules (using the same "slots/blocks" as their parent
● Message expansion modules
[6 empty] | ● Telphone Class A NAC Adapter |  | 1273
● Worst Case Load
● Standby Load = 0.0000, Alarm Load = 0.0000
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0000
● Mount on Phone or Expansion Phone module
● One per a Phone or Expansion Phone module
[6 empty] | ● Network Media module (6 types) |  | 6056
● Worst Case Load
● Standby Load = 0.0550, Alarm Load = 0.0550
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0550
● Mounts on legacy Network module
● 1 Min, 2 Max per Network module
[6 empty] | ● Flex Amp Expansion NAC board |  | 1245
● Worst Case Load
● Standby Load = 0.0084, Alarm Load = 0.0600
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0600
● Addes 3 Class B NACs
● 1 Max per Flex Amplifier
● Mounts on Flex Amplifier
● Modules that mount in the Behind the Door Plane
● 4” x 4” modules that mount on a metal bracket behind the Door
● Must mount in cabinet with a glass door
● Must mount Left to Right
● Cannot place behind the Fire Phone Enclosure, Microphone Enclosure or Panel Mounted Printer
● Cannot place in front of Legacy modules, Power Supplies or Amplifiers
[6 empty] | ● 64/64 LED/Switch Controller module |  | 1288
● Worst Case Load
● Standby Load = 0.0200, Alarm Load = 0.0200
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0200
● One per bay
● Cannot mount in a CPU bay
● Supports a total of 64 LEDs or switches
● For the 1st set of 64 LEDs AND/OR switches
● Contains the module and a mounting bracket for the back of the door
● Mounts in Block A, Block C, or Block E
● Required for any bay with LED/Switch modules
● Spares are allowed
[6 empty] | ● Expansion 64/64 LED/Switch Controller module |  | 1289
● Worst Case Load
● Standby Load = 0.0200, Alarm Load = 0.0200
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0200
● One per bay
● Cannot mount in a CPU bay
● Supports a total of 64 LEDs or switches
● For the 2nd set of 64 LEDs AND/OR switches
● Mounts on the mounting bracket supplied by the 64/64 LED/Switch Controller
[6 empty] | ● Mounts in Block B, Block D, or Block F (Block is "paired" with the 64/64 LED/Switch Controller's block) | x x
● Required for any bay with LED/Switch modules (> 64 LED/Switches)
● Requires a 64/64 LED/Switch Controller module
● Spares are allowed (but must be paired with the 64/64 LED/Switch Controller module)
● Modules that mount in the Front of the Door Plane
● Must mount in cabinet with a glass door
● Must mount Left to Right
[6 empty] | ● LED/Switch modules – 2” x 10” or 4” x 10” |  | 1280
● Worst Case Load
● Standby Load = 0.0000, Alarm Load = 0.0240
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0240
● 2"x10" modules mount in Slot1, Slot2, Slot3, Slot4, Slot5, Slot6, Slot7, Slot8
● 4"x10" modules mount in Slot12, Slot23, Slot34, Slot45, Slot56, Slot67, Slot78
● Number of LED and Switches per a modules differ
● LEDs per modules
● 0, 8, 16, 24
● Switches per modules
● 0, 8, 16, 24
● 16SW/16LED module must mount left of an 8SW/8LED or 8SW/16LED module
[6 empty] | ● Audio LED/Switch modules – 2” x 10” |  | 1252
● Worst Case Load
● Standby Load = 0.0000, Alarm Load = 0.0240
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0240
● 1 Max
● Must place right of Microphone if ordered
● Mount in Slot1, Slot2, Slot3, Slot4, Slot5, Slot6, Slot7, Slot8
[6 empty] | ● Panel Mounted Printer |  | 1293
● Worst Case Load
● Standby Load = 0.0000, Alarm Load = 0.0000
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0000
● 1 max
● Takes up 3 slots
● Requires and RS323 module (unrestricted placement)
● Only ES modules allowed behind it on the Back Plane
[6 empty] | ● Microphone – 4” x 10” and 5” deep |  | 1243
● Worst Case Load
● Standby Load = 0.0024, Alarm Load = 0.0060
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0060
● Required 64/64 Controller in same Bay
● Requires Audio Controller in same Bay
● Mounts in Slot12
[6 empty] | ● Fire Fighter Phones – 4” x 10” and 5” deep |  | 1270
● Worst Case Load
● Standby Load = 0.0800, Alarm Load = 0.1400
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0000
● 1 max
● Needs 1 Address (phone module)
● Includes two modules
● Fire Fighter Phone Enclosure
● In a panel with an Audio Controller Bay:
● If no Microphone ordered, mounts in Slot12 of Audio Controller bay
● If Microphone ordered, mounts in Slot56 of Audio Controller bay
● In a panel without an Audio Controller Bay:
● Mounts in Bay 2 Slot12
● Phone module
● Mounts in Block E
● Must mount in same bay as the Enclosure
● Display – 16” x 10” x ½”
● Take up the whole Front of Door Plane and Behind the Door Plane
● Included, as indicated above, with some panels
● 1st display mounts in Box 1 Bay 1
● 2nd display mounts in Box 1 Bay 2
[6 empty] | ● Classic Display (2x40 Display) |  | mckey
● Worst Case Load
● Standby Load = 0.0100, Alarm Load = 0.0450
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.0450
[6 empty] | ● InfoAlarm Display |  | FUI
● Worst Case Load
● Standby Load = 0.0820, Alarm Load = 0.1150
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.1150
● Needs 1 address
● No Display
● Automatically filled with eight (8) Blank Filler Modules
[6 empty] | ● Remote Command Center – 16” x 10” x ½” |  | 1292
● Worst Case Load
● Standby Load = 0.1750, Alarm Load = 0.2000
● Card Power
● Card Power Available = 0.0000, Card Power Consumed = 0.2000
● With Remote Annunciator panels only
● Take up the whole Front of Door Plane and Behind the Door Plane
● Needs 1 address
● Only ES modules allowed behind it on the Back Plane
● ESPS must mount in Bay 2
[6 empty] | ● Blank Filler Modules - 2” x 10” or 16” x 10” |  | 1279
● Blank Filler Module - 2" x 10"
● Required selection for all open display frame slots (automatically caluclated and placed)
[6 empty] | ● Blank Filler Panel = 16" x 10" |  | 2302
● Automatically added for any expansion bay without modules
● Chaissis and Blank Filler Panel are mutually exclusive
● Other
[6 empty] | ● Chaissis |  | 2300
● Automatically added for any expansion bay that has modules
[6 empty] | ● Audio Expansion Bay Harness |  | 2320
[6 empty] | ● Added for each expansion bay that contains Audio modules (controller, amps, etc) - exception is the bay that contains the Audio Controller | x x
[6 empty] | ● Expansion Bay Stablizer Bracket |  | 2303
● Included for each expansion bay that contrains legacy module
[6 empty] | ● ESPS PDM Harness |  | 644
● Must have one per a power supply
[6 empty] | ● Power Distribution module |  | 634
● One per cabinet
[6 empty] | ● Power/Comm Box to Box Harness |  | 636
[6 empty] | ● Needs 1 per expansion Cabinet plus 1 per every bay that contains a 64/64 LED/SW controller module and two Flex Amplifiers | x x
[6 empty] | ● Audio Box to Box Harness |  | 637
● Requires 1 per expansion Cabinet that contains audio modules or amplifiers
[6 empty] | ● Additional 24V Harness |  | 638
● Requires 1 per expansion bays that contain Legacy modules
[6 empty] | ● MX Loop Card Power Supply Harness |  | 642
● 1 Max
● Mounts in Box 1 Bay 2 Block G (Block H is reserved)
● Requried if MX Digital Loop modules in Box 1 Bay 2 without an ESPS
[6 empty] | ● Incident Commander Mounting Bay |  | 7909
● Place holder
● Reserves all of Cab 1 Bay 2
● Doesn't require an expansion bay
[6 empty] | ● System without DACT |  | 7908
[6 empty] | ● "SDACT module" and "System without Dact" are mutually exclusive, and each CPU panel must have one or the other. | x x
● Not allowed on Transponders or Annunciator Panel
● Default selection for International CPU panels, but can be manually removed
● Optional selection for Domestic and Canadian CPU panel (not allowed if SDACT module ordered)