## Sheet1
Module Model Number | Description | compatible with Panel | compatible with Protocol | Total Point Capacity Possible | Point Capacity / Circuit Capacity | Supervisory Current | Alarm Current | Supports which Speakers | Circuits/Points | Possible Compulsory Main Modules | Is it Main module or sub-module mounted on main | Physical Size | Mounted ON | Another Module needed to function | Specification Descriptions | Keywords associated with the module
4081-9018 | End-of-line resistor for 70.7 VRMS NACs; 10 kΩ, 1 W | 4100ES |  |  | EOL for supervised speaker circuits | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4081-9018 | End-of-line resistor for 70.7 VRMS NACs; 10 kΩ, 1 W | 4100ES |  |  | EOL for supervised speaker circuits | [7 empty] | Internal |  |  | Master Controller
4100-0156 | 8 VDC Converter (required for multiple Physical Bridge Modules) | 4100ES |  |  | 3 A max | [6 empty] | 1 Block | Internal |  | Included with loads | Master Controller
4100-0156 | 8 VDC Converter (required for multiple Physical Bridge Modules) | 4100ES |  |  | 3 A max | [6 empty] | 1 Block | Internal |  | Included with loads | PS Accessories
4100-0623 | Network Audio Riser Controller Module (-0621 analog, -0622 digital) | 4100ES |  |  | Controls riser module for audio distribution | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-0623 | Network Audio Riser Controller Module (-0621 analog, -0622 digital) | 4100ES |  |  | Controls riser module for audio distribution | [7 empty] | Internal |  |  | Master Controller
4100-0636 | Power & Communications Harness Kit (for LED/switch controllers when two Flex-35/50 amps + SPS share bay) | 4100ES | [10 empty] | Door |  |  | LED-Switch (4100-0032)
4100-0636 | Power & Communications Harness Kit (for LED/switch controllers when two Flex-35/50 amps + SPS share bay) | 4100ES | [10 empty] | Door |  |  | Master Controller
4100-0641 | 26‑position flex cable (14.5 in.) | 4100ES | [10 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-0641 | 26‑position flex cable (14.5 in.) | 4100ES | [10 empty] | Internal |  |  | Master Controller
4100-0642 | MX Loop Interface Power Harness (feeds up to three 4100-6311 in second bay) | 4100ES | MX | [7 empty] | Sub-module | Harness | Internal | 4100-6311 | Required in second bay power sharing | S4100-0059
4100-1210 | Analog controller board only | 4100ES |  |  | Mounts in Blocks A and B | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1210 | Analog controller board only | 4100ES |  |  | Mounts in Blocks A and B | [7 empty] | Internal |  |  | Master Controller
4100-1240 | Auxiliary Audio Input Module; four additional inputs | 4100ES |  |  | Adds 4 audio inputs | [7 empty] | Internal |  |  | Master Controller
4100-1240 | Auxiliary Audio Input Module; four additional inputs | 4100ES |  |  | Adds 4 audio inputs | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1241 | 8 Minute Message Expansion Module | 4100ES |  |  | Adds 8 minutes of message storage | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1241 | 8 Minute Message Expansion Module | 4100ES |  |  | Adds 8 minutes of message storage | [7 empty] | Internal |  |  | Master Controller
4100-1242 | 32 Minute Message Expansion Module | 4100ES |  |  | Adds 32 minutes of message storage | [7 empty] | Internal |  |  | Master Controller
4100-1242 | 32 Minute Message Expansion Module | 4100ES |  |  | Adds 32 minutes of message storage | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1243 | Master Microphone Module; one max per audio system; mounts on front panel | 4100ES |  |  |  | 2.4 | 6 |  |  |  |  | Requires 2 Slots in expansion bay (space behind for flat modules only) | Both |  |  | Master Controller
4100-1243 | Master Microphone Module; one max per audio system; mounts on front panel | 4100ES |  |  |  | 2.4 | [5 empty] | Requires 2 Slots in expansion bay (space behind for flat modules only) | Both |  |  | VCC Interfaces (S4100-0104)
4100-1245 | Flex-35/50 NAC Expansion Module | 4100ES |  |  | Adds 3 Class B, 1.5 A NACs (audio) for Flex-35/50 | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1245 | Flex-35/50 NAC Expansion Module | 4100ES |  |  | Adds 3 Class B, 1.5 A NACs (audio) for Flex-35/50 | [7 empty] | Internal |  |  | Master Controller
4100-1246 | Flex-35/50 Class A Adapter for 3 NACs | 4100ES |  |  | Class A conversion of Flex‑35/50 audio NACs | [7 empty] | Internal |  |  | Master Controller
4100-1246 | Flex-35/50 Class A Adapter for 3 NACs | 4100ES |  |  | Class A conversion of Flex‑35/50 audio NACs | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1248 | 100 W Amplifier NAC Expansion Module | 4100ES |  |  | Adds 6 Class B, 2 A NACs (audio) for 100 W amplifiers | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1248 | 100 W Amplifier NAC Expansion Module | 4100ES |  |  | Adds 6 Class B, 2 A NACs (audio) for 100 W amplifiers | [7 empty] | Internal |  |  | Master Controller
4100-1249 | 100 W Amplifier Class A Adapter Module for 6 NACs | 4100ES |  |  | Class A conversion of 100 W amplifier audio NACs | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1249 | 100 W Amplifier Class A Adapter Module for 6 NACs | 4100ES |  |  | Class A conversion of 100 W amplifier audio NACs | [7 empty] | Internal |  |  | Master Controller
4100-1252 | 1 Channel (audio or microphone) operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Both |  |  | Master Controller
4100-1252 | 1 Channel (audio or microphone) operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Both |  |  | VCC Interfaces (S4100-0104)
4100-1253 | 1.5 Channel (audio + microphone) operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Both |  |  | Master Controller
4100-1253 | 1.5 Channel (audio + microphone) operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Both |  |  | VCC Interfaces (S4100-0104)
4100-1254 | 2 Channel (full audio) operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Internal |  |  | VCC Interfaces (S4100-0104)
4100-1254 | 2 Channel (full audio) operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Internal |  |  | Master Controller
4100-1255 | 3–8 Channel operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Internal |  |  | VCC Interfaces (S4100-0104)
4100-1255 | 3–8 Channel operator interface | 4100ES |  |  | Single slot; requires LED/switch controller | [7 empty] | Internal |  |  | Master Controller
4100-1259 | Constant Supervision Adapter for 25 VRMS amplifiers | 4100ES | [10 empty] | Internal |  |  | Master Controller
4100-1259 | Constant Supervision Adapter for 25 VRMS amplifiers | 4100ES | [10 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1260 | Constant Supervision Adapter for 70.7 VRMS amplifiers | 4100ES | [10 empty] | Internal |  |  | Master Controller
4100-1260 | Constant Supervision Adapter for 70.7 VRMS amplifiers | 4100ES | [10 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1266 | NAC Extender for Expansion Signal Module | 4100ES |  |  | Expands each 5116 card to 6 Class B NACs | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1266 | NAC Extender for Expansion Signal Module | 4100ES |  |  | Expands each 5116 card to 6 Class B NACs | [7 empty] | Internal |  |  | Master Controller
4100-1267 | Class A Adapter for Expansion Signal Module | 4100ES |  |  | Enables Class A operation on 5116 outputs | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1267 | Class A Adapter for Expansion Signal Module | 4100ES |  |  | Enables Class A operation on 5116 outputs | [7 empty] | Internal |  |  | Master Controller
4100-1268 | Constant Supervision Adapter | 4100ES |  |  | For supervised audio speaker circuits | [7 empty] | Internal |  |  | Audio Options (S4100-0104)
4100-1268 | Constant Supervision Adapter | 4100ES |  |  | For supervised audio speaker circuits | [7 empty] | Internal |  |  | Master Controller
4100-1270 | Master Telephone with Telephone Control Module and 3 Class B telephone NACs; for FACP | 4100ES |  |  | One max per audio system; front panel module + telephone control module mounts on bay plate | [6 empty] | Front module + bay plate | Internal |  |  | Master Controller
4100-1270 | Master Telephone with Telephone Control Module and 3 Class B telephone NACs; for FACP | 4100ES |  |  | One max per audio system; front panel module + telephone control module mounts on bay plate | [6 empty] | Front module + bay plate | Internal |  |  | Telephone (S4100-0104)
4100-1272 | Telephone Module with 3 phone NACs | 4100ES |  |  | Three Class B telephone NACs | [6 empty] | Single Block module; mounts to bay mounting plate | Internal |  |  | Telephone (S4100-0104)
4100-1272 | Telephone Module with 3 phone NACs | 4100ES |  |  | Three Class B telephone NACs | [6 empty] | Single Block module; mounts to bay mounting plate | Internal |  |  | Master Controller
4100-1273 | Telephone Class A Adapter Module | 4100ES |  |  | Converts 1272 to Class A | [6 empty] | Mounts to 4100-1272; no extra space | Internal |  |  | Master Controller
4100-1273 | Telephone Class A Adapter Module | 4100ES |  |  | Converts 1272 to Class A | [6 empty] | Mounts to 4100-1272; no extra space | Internal |  |  | Telephone (S4100-0104)
4100-1275 | 8 function HOA with labeled switches (G/R/W LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1275 | 8 function HOA with labeled switches (G/R/W LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Door |  |  | Master Controller
4100-1276 | 8-LED module (red LEDs) | 4100ES |  |  | 8 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1276 | 8-LED module (red LEDs) | 4100ES |  |  | 8 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1277 | 16-LED module (red/yellow LEDs) | 4100ES |  |  | 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1277 | 16-LED module (red/yellow LEDs) | 4100ES |  |  | 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1278 | 16 switches with 16 LEDs (red-yellow) | 4100ES |  |  | 16 switches / 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1278 | 16 switches with 16 LEDs (red-yellow) | 4100ES |  |  | 16 switches / 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1279 | Single blank 2" display cover | 4100ES | [10 empty] | Internal |  |  | Master Controller
4100-1279 | Single blank 2" display cover | 4100ES | [10 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-1280 | 8 switches with 8 LEDs (red) | 4100ES |  |  | 8 switches / 8 LEDs | [6 empty] | Panel-mounted | Door |  |  | LED-Switch (4100-0032)
4100-1280 | 8 switches with 8 LEDs (red) | 4100ES |  |  | 8 switches / 8 LEDs | [6 empty] | Panel-mounted | Door |  |  | Master Controller
4100-1281 | 8 switches with 8 LEDs (yellow) | 4100ES |  |  | 8 switches / 8 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1281 | 8 switches with 8 LEDs (yellow) | 4100ES |  |  | 8 switches / 8 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1282 | 8 switches with 16 LEDs (red/yellow) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1282 | 8 switches with 16 LEDs (red/yellow) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1283 | 8 switches with 16 LEDs (yellow/yellow) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1283 | 8 switches with 16 LEDs (yellow/yellow) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1284 | 8 switches with 16 LEDs (red/green) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1284 | 8 switches with 16 LEDs (red/green) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1285 | 16 switches with 16 LEDs (red) | 4100ES |  |  | 16 switches / 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1285 | 16 switches with 16 LEDs (red) | 4100ES |  |  | 16 switches / 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1286 | 8 function HOA (On/Off/Auto) with labeled switches (G/R/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Door |  |  | Master Controller
4100-1286 | 8 function HOA (On/Off/Auto) with labeled switches (G/R/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1288 | 64 LED/64 Switch Controller w/ mounting plate | 4100ES |  |  | Controls up to 64 LEDs & 64 switches; mounts behind LED/switch modules | [6 empty] | Controllers per bay: 2 max; same bay as LED/switch modules | Door |  |  | LED-Switch (4100-0032)
4100-1288 | 64 LED/64 Switch Controller w/ mounting plate | 4100ES |  |  | Controls up to 64 LEDs & 64 switches; mounts behind LED/switch modules | [6 empty] | Controllers per bay: 2 max; same bay as LED/switch modules | Door |  |  | Master Controller
4100-1289 | 64 LED/64 Switch Controller without plate (adds to 1288) | 4100ES |  |  | Adds another 64 LEDs & 64 switches | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1289 | 64 LED/64 Switch Controller without plate (adds to 1288) | 4100ES |  |  | Adds another 64 LEDs & 64 switches | [7 empty] | Door |  |  | Master Controller
4100-1290 | Selectable input/output points for external connections | 4100ES |  |  | 24 points; output 150 mA @ 24 VDC per point | 34 | [6 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-1290 | Selectable input/output points for external connections | 4100ES |  |  | 24 points; output 150 mA @ 24 VDC per point | 34 | 75 | [5 empty] | Internal |  |  | Master Controller
4100-1291 | Un-isolated Remote Unit Interface (RUI) module | 4100ES |  |  | Up to 3 per panel; up to 31 remote devices per controller via RUI/RUI+ | 85 | 85 |  |  |  |  | 1 Slot | Internal |  |  | Master Controller
4100-1291 | Un-isolated Remote Unit Interface (RUI) module | 4100ES |  |  | Up to 3 per panel; up to 31 remote devices per controller via RUI/RUI+ | 85 | 85 |  |  |  |  | 1 Slot | Internal |  |  | Comm-City-DACT
4100-1293 | Panel‑mount thermal printer | 4100ES |  |  | 40‑col paper, 1.33 in/s; 312 cps | 125 | [5 empty] | Requires 3 expansion slots | Door |  | 19–33 VDC; RS‑232 9600 baud | LED-Switch (4100-0032)
4100-1293 | Panel‑mount thermal printer | 4100ES |  |  | 40‑col paper, 1.33 in/s; 312 cps | 125 | 800 |  |  |  |  | Requires 3 expansion slots | Door |  | 19–33 VDC; RS‑232 9600 baud | Master Controller
4100-1294 | LED/Switch slide‑in labels; order one per cabinet | 4100ES | [10 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1294 | LED/Switch slide‑in labels; order one per cabinet | 4100ES | [10 empty] | Door |  |  | Master Controller
4100-1295 | 8 function HOA, unlabeled (G/R/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Internal |  |  | Master Controller
4100-1295 | 8 function HOA, unlabeled (G/R/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-1296 | 8 switches with 16 LEDs (green/yellow) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1296 | 8 switches with 16 LEDs (green/yellow) | 4100ES |  |  | 8 switches / 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1299 | 8 function HOA, unlabeled (G/R/W LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-1299 | 8 function HOA, unlabeled (G/R/W LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Internal |  |  | Master Controller
4100-1300 | 16 switches with 16 pluggable LEDs (red/yellow) | 4100ES |  |  | 16 switches / 16 LEDs | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1300 | 16 switches with 16 pluggable LEDs (red/yellow) | 4100ES |  |  | 16 switches / 16 LEDs | [7 empty] | Door |  |  | Master Controller
4100-1301 | 8 function HOA, unlabeled (G/Y/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Internal |  |  | Master Controller
4100-1301 | 8 function HOA, unlabeled (G/Y/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-1302 | 8 function HOA with labeled switches (G/Y/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Door |  |  | Master Controller
4100-1302 | 8 function HOA with labeled switches (G/Y/G LEDs) | 4100ES |  |  | 8 HOA functions | [7 empty] | Door |  |  | LED-Switch (4100-0032)
4100-1312 | 50 W @ 25 VRMS; constant supervision compatible | 4100ES |  |  | Includes three on‑board Class B audio NACs; NAC rating 2 A | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1312 | 50 W @ 25 VRMS; constant supervision compatible | 4100ES |  |  | Includes three on‑board Class B audio NACs; NAC rating 2 A | [7 empty] | Internal |  |  | Master Controller
4100-1313 | 50 W @ 70.7 VRMS; constant supervision compatible | 4100ES |  |  | Includes three on‑board Class B audio NACs; NAC rating 0.707 A | [7 empty] | Internal |  |  | Master Controller
4100-1313 | 50 W @ 70.7 VRMS; constant supervision compatible | 4100ES |  |  | Includes three on‑board Class B audio NACs; NAC rating 0.707 A | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1314 | 100 W @ 25 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers; 2 A @ 25 VRMS | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1314 | 100 W @ 25 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers; 2 A @ 25 VRMS | [7 empty] | Internal |  |  | Master Controller
4100-1315 | 100 W @ 70.7 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers; 1.4 A @ 70.7 VRMS | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1315 | 100 W @ 70.7 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers; 1.4 A @ 70.7 VRMS | [7 empty] | Internal |  |  | Master Controller
4100-1320 | 100 W @ 25 VRMS, 120 VAC | 4100ES |  |  | Uses NACs of primary amplifier | [7 empty] | Internal |  |  | Master Controller
4100-1320 | 100 W @ 25 VRMS, 120 VAC | 4100ES |  |  | Uses NACs of primary amplifier | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1321 | 100 W @ 70.7 VRMS, 120 VAC | 4100ES |  |  | Uses NACs of primary amplifier | [7 empty] | Internal |  |  | Master Controller
4100-1321 | 100 W @ 70.7 VRMS, 120 VAC | 4100ES |  |  | Uses NACs of primary amplifier | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1324 | 100 W @ 25 VRMS, 220/230/240 VAC | 4100ES | [10 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1324 | 100 W @ 25 VRMS, 220/230/240 VAC | 4100ES | [10 empty] | Internal |  |  | Master Controller
4100-1325 | 100 W @ 70.7 VRMS, 220/230/240 VAC | 4100ES | [10 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1325 | 100 W @ 70.7 VRMS, 220/230/240 VAC | 4100ES | [10 empty] | Internal |  |  | Master Controller
4100-1326 | 50 W @ 25 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 2 A | Power from XPS/SPS/RPS | [5 empty] | 50 W | Internal |  |  | Master Controller
4100-1326 | 50 W @ 25 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 2 A | [7 empty] | Internal |  | 50 W | Digital Amps (S4100-0104)
4100-1327 | 50 W @ 70.7 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 0.707 A | Power from XPS/SPS/RPS | [5 empty] | 50 W | Internal |  |  | Master Controller
4100-1327 | 50 W @ 70.7 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 0.707 A | [7 empty] | Internal |  | 50 W | Digital Amps (S4100-0104)
4100-1328 | 100 W @ 25 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers max; 2 A @ 25 VRMS | [7 empty] | Internal | 4100-1260 | Primary 100 W | Digital Amps (S4100-0104)
4100-1328 | 100 W @ 25 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers max; 2 A @ 25 VRMS | Use 4100-1260 supervision adapter for 70.7 V (if used) | UL listing |  |  |  |  | Primary 100 W | Internal |  |  | Master Controller
4100-1329 | 100 W @ 70.7 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers max; 1.4 A @ 70.7 VRMS |  | UL listing |  |  |  |  | Primary 100 W | Internal |  |  | Master Controller
4100-1329 | 100 W @ 70.7 VRMS with PSU; constant supervision compatible | 4100ES |  |  | Six Class B audio NACs; NAC rating 50 W or 100 speakers max; 1.4 A @ 70.7 VRMS | [7 empty] | Internal |  | Primary 100 W | Digital Amps (S4100-0104)
4100-1332 | 100 W @ 25 VRMS, 220/230/240 VAC | 4100ES |  |  | Six Class B audio NACs; NAC 50 W or 100 speakers; 2 A @ 25 VRMS | [7 empty] | Internal |  |  | Master Controller
4100-1332 | 100 W @ 25 VRMS, 220/230/240 VAC | 4100ES |  |  | Six Class B audio NACs; NAC 50 W or 100 speakers; 2 A @ 25 VRMS | [7 empty] | Internal |  |  | Digital Amps (S4100-0104)
4100-1333 | 100 W @ 70.7 VRMS, 220/230/240 VAC | 4100ES |  |  | Six Class B audio NACs; NAC 50 W or 100 speakers; 1.4 A @ 70.7 VRMS | [7 empty] | Internal |  |  | Master Controller
4100-1333 | 100 W @ 70.7 VRMS, 220/230/240 VAC | 4100ES |  |  | Six Class B audio NACs; NAC 50 W or 100 speakers; 1.4 A @ 70.7 VRMS | [7 empty] | Internal |  |  | Digital Amps (S4100-0104)
4100-1334 | 100 W @ 25 VRMS, 120 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Digital Amps (S4100-0104)
4100-1334 | 100 W @ 25 VRMS, 120 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Master Controller
4100-1335 | 100 W @ 70.7 VRMS, 120 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Digital Amps (S4100-0104)
4100-1335 | 100 W @ 70.7 VRMS, 120 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Master Controller
4100-1338 | 100 W @ 25 VRMS, 220/230/240 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Digital Amps (S4100-0104)
4100-1338 | 100 W @ 25 VRMS, 220/230/240 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Master Controller
4100-1339 | 100 W @ 70.7 VRMS, 220/230/240 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Digital Amps (S4100-0104)
4100-1339 | 100 W @ 70.7 VRMS, 220/230/240 VAC | 4100ES |  |  | Uses the six Class B NACs of primary amplifier | [7 empty] | Internal |  |  | Master Controller
4100-1361 | 35 W @ 25 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 1.4 A; 35 W or 100 speakers | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-1361 | 35 W @ 25 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 1.4 A; 35 W or 100 speakers | [7 empty] | Internal |  |  | Master Controller
4100-1362 | 35 W @ 70.7 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 0.5 A | [7 empty] | Internal |  |  | Master Controller
4100-1362 | 35 W @ 70.7 VRMS; constant supervision compatible | 4100ES |  |  | NAC rating 0.5 A | [7 empty] | Internal |  |  | Analog Audio (S4100-0104)
4100-2504 | IP communicator (side mount or vertical mount) | 4100ES | [9 empty] | 1 slot (2504) / 2 blocks (2506) | Internal |  |  | Master Controller
4100-2504 | IP communicator (side mount or vertical mount) | 4100ES | [9 empty] | 1 slot (2504) / 2 blocks (2506) | Internal |  |  | Comm-City-DACT
4100-2506 | IP communicator (side mount or vertical mount) | 4100ES | [9 empty] | 1 slot (2504) / 2 blocks (2506) | Internal |  |  | Comm-City-DACT
4100-2506 | IP communicator (side mount or vertical mount) | 4100ES | [9 empty] | 1 slot (2504) / 2 blocks (2506) | Internal |  |  | Master Controller
4100-3102 | 127 point capacity | 4100ES | IDNet |  | Device load 1.7 mA each | 255 | 275 |  |  |  |  | 2 Slots | Internal |  | Fully loaded totals: 471 mA standby / 491 mA alarm | MAPNET Modules
4100-3103 | Isolator Module; converts one SLC into four isolated outputs (Class A or B) | 4100ES | IDNet |  | Up to two isolators per SLC | 50 | 50 |  |  |  |  | 1 Slot | Internal |  |  | MAPNET Modules
4100-3109 | Electrically isolated output; two short‑circuit‑isolating loops; 250 point capacity | 4100ES | IDNet |  | Capacity by devices connected (see currents) | 50 (no devices) / 90 (50) / 150 (125) / 250 (250) | 60 (no devices) / 150 (50) / 225 (125) / 350 (250) |  |  |  |  | 1 Block | Internal |  | Per-device: 0.8 mA standby; 1.0 mA alarm LED off; 3.0 mA alarm LED on (max 20 LEDs on) | Master Controller
4100-3109 | Electrically isolated output; two short‑circuit‑isolating loops; 250 point capacity | 4100ES | IDNet |  | Capacity by devices connected (see currents) | 50 (no devices) / 90 (50) / 150 (125) / 250 (250) | 60 (no devices) / 150 (50) / 225 (125) / 350 (250) |  |  |  |  | 1 Block | Internal |  | Per-device: 0.8 mA standby; 1.0 mA alarm LED off; 3.0 mA alarm LED on (max 20 LEDs on) | IDNet Modules
4100-3110 | Electrically isolated output; four short‑circuit‑isolating loops; 250 point capacity | 4100ES | IDNet |  | Capacity by devices connected (see currents) | 50 / 90 / 150 / 250 (for 0/50/125/250 devices) | 60 / 150 / 225 / 350 (for 0/50/125/250 devices) |  |  |  |  | 1 Block | Internal |  | Per-device draw as above | IDNet Modules
4100-3110 | Electrically isolated output; four short‑circuit‑isolating loops; 250 point capacity | 4100ES | IDNet |  | Capacity by devices connected (see currents) | 50 / 90 / 150 / 250 (for 0/50/125/250 devices) | 60 / 150 / 225 / 350 (for 0/50/125/250 devices) |  |  |  |  | 1 Block | Internal |  | Per-device draw as above | Master Controller
4100-3111 | IDNet Short Circuit Isolating Loop Output (mount up to two on 4100-3109 or -3117) | 4100ES | IDNet |  | Increases initiating SLC count (total initiating SLCs per CPU, incl. VESDA interface: 30) | [7 empty] | Internal | 4100-3109, 4100-3117 |  | IDNet Modules
4100-3111 | IDNet Short Circuit Isolating Loop Output (mount up to two on 4100-3109 or -3117) | 4100ES | IDNet |  | Increases initiating SLC count (total initiating SLCs per CPU, incl. VESDA interface: 30) | [7 empty] | Internal | 4100-3109, 4100-3117 |  | Master Controller
4100-3117 | Electrically isolated output; two short‑circuit‑isolating loops; 250 point capacity | 4100ES | IDNet |  | Capacity by devices connected (see currents) | 50 (no devices) / 90 (50) / 150 (125) / 250 (250) | 60 (no devices) / 150 (50) / 225 (125) / 350 (250) |  |  |  |  | 1 Block | Internal |  | Per-device: 0.8 mA standby; 1.0 mA alarm LED off; 3.0 mA alarm LED on (max 20 LEDs on) | IDNet Modules
4100-3117 | Electrically isolated output; two short‑circuit‑isolating loops; 250 point capacity | 4100ES | IDNet |  | Capacity by devices connected (see currents) | 50 (no devices) / 90 (50) / 150 (125) / 250 (250) | 60 (no devices) / 150 (50) / 225 (125) / 350 (250) |  |  |  |  | 1 Block | Internal |  | Per-device: 0.8 mA standby; 1.0 mA alarm LED off; 3.0 mA alarm LED on (max 20 LEDs on) | Master Controller
4100-3207 | Four DPDT with feedback | 4100ES |  |  | Resistive 2 A @ 30 VDC/30 VAC; Inductive 0.5 A @ 30 VDC or 120 VAC | 18 | 65 |  |  |  |  | 1 Block | Internal |  |  | Relay Modules
4100-3207 | Four DPDT with feedback | 4100ES |  |  | Resistive 2 A @ 30 VDC/30 VAC; Inductive 0.5 A @ 30 VDC or 120 VAC | 18 | 65 |  |  |  |  | 1 Block | Internal |  |  | Master Controller
4100-3208 | Four DPDT with feedback (10 A) | 4100ES |  |  | Resistive/Inductive 10 A @ 30 VDC/120/240 VAC | 20 | 188 |  |  |  |  | 2 Slots | Internal |  |  | Master Controller
4100-3208 | Four DPDT with feedback (10 A) | 4100ES |  |  | Resistive/Inductive 10 A @ 30 VDC/120/240 VAC | 20 | 188 |  |  |  |  | 2 Slots | Internal |  |  | Relay Modules
4100-3209 | Eight SPDT switches | 4100ES |  |  | Resistive 3 A @ 30 VDC or 120 VAC; Inductive 1.5 A @ 30 VDC or 120 VAC | 16 | 200 |  |  |  |  | 1 Block | Door |  |  | Master Controller
4100-3209 | Eight SPDT switches | 4100ES |  |  | Resistive 3 A @ 30 VDC or 120 VAC; Inductive 1.5 A @ 30 VDC or 120 VAC | 16 | 200 |  |  |  |  | 1 Block | Door |  |  | Relay Modules
4100-5013 | 8-point zone/relay module; each zone selectable as IDC or Relay | 4100ES |  |  | Up to eight Class B IDCs or four Class A IDCs; or up to 8 relays (2 A resistive @ 30 VDC) | 83 | 295 |  |  |  |  | 1 Block | Internal | 4100-5130, 4100-6305 |  | Master Controller
4100-5013 | 8-point zone/relay module; each zone selectable as IDC or Relay | 4100ES |  |  | Up to eight Class B IDCs or four Class A IDCs; or up to 8 relays (2 A resistive @ 30 VDC) | 83 | 295 |  |  |  |  | 1 Block | Internal | 4100-5130, 4100-6305 |  | 8-Point Zone-Relay
4100-5116 | Expansion Signal Module; three, 1.5 A audio NACs | 4100ES |  |  | 3 Class B audio NACs, 1.5 A each | [7 empty] | Internal | 4100-1266, 4100-1267 |  | Master Controller
4100-5116 | Expansion Signal Module; three, 1.5 A audio NACs | 4100ES |  |  | 3 Class B audio NACs, 1.5 A each | [7 empty] | Internal | 4100-1266, 4100-1267 |  | Audio Options (S4100-0104)
4100-5130 | Voltage Regulator Module, 22.8–26.4 VDC (25 V nominal); isolated/resettable; earth detection + trouble relay | 4100ES | [9 empty] | 1 Block | Internal |  | 3 A max (2.5 A load) / 4.9 A max (4 A load) | Master Controller
4100-5130 | 25 V Regulator Module (isolated/resettable; earth fault detect) | 4100ES |  |  |  | 3000 | 4900 | 25 VRMS |  |  | Sub-module | 1 Block (internal) | Internal | 4100-6305 | 22.8–26.4 VDC; 3 A max (2.5 A load) / 4.9 A (4.0 A load) | S4100-0059
4100-5130 | Voltage Regulator Module, 22.8–26.4 VDC (25 V nominal); isolated/resettable; earth detection + trouble relay | 4100ES | [9 empty] | 1 Block | Internal |  | 3 A max (2.5 A load) / 4.9 A max (4 A load) | PS Accessories
4100-5131 | ES-PS Fan Module (allows >1 PS in a bay; may increase DC output capacity) | 4100ES |  |  |  | 0 | 200 | [5 empty] | Internal |  |  | PS Accessories
4100-5131 | ES-PS Fan Module (allows >1 PS in a bay; may increase DC output capacity) | 4100ES |  |  |  | 0 | 200 | [5 empty] | Internal |  |  | Master Controller
4100-5152 | 12 VDC Power Option | 4100ES |  |  | 2 A max | [6 empty] | 1 Block | Internal |  | 2 A max output | PS Accessories
4100-5152 | 12 VDC Power Option | 4100ES |  |  | 2 A max | [6 empty] | 1 Block | Internal |  | 2 A max output | Master Controller
4100-5311 | 9 A EPS with IDNet 2 (250 pt) + 3 x IDNAC + 2 A aux; 120 VAC | 4100ES | IDNAC |  | Right side add IDNet device currents separately | 225 | [5 empty] | 4 Blocks | Internal |  |  | EPS & Accessories
4100-5311 | 9 A EPS with IDNet 2 (250 pt) + 3 x IDNAC + 2 A aux; 120 VAC | 4100ES | IDNAC |  | Right side add IDNet device currents separately | 225 | 490 |  |  |  |  | 4 Blocks | Internal |  |  | Master Controller
4100-5313 | As above; 220–240 VAC | 4100ES |  |  | Right side add IDNet device currents separately | [6 empty] | 4 Blocks | Internal |  |  | Master Controller
4100-5313 | As above; 220–240 VAC | 4100ES |  |  | Right side add IDNet device currents separately | [6 empty] | 4 Blocks | Internal |  |  | EPS & Accessories
4100-5325 | 9 A Expansion EPS; same as EPS without IDNet 2 | 4100ES | IDNet |  |  | 125 | [5 empty] | 4 Blocks | Internal |  |  | EPS & Accessories
4100-5325 | 9 A Expansion EPS; same as EPS without IDNet 2 | 4100ES | IDNet |  |  | 125 | 220 |  |  |  |  | 4 Blocks | Internal |  |  | Master Controller
4100-5327 | As above; 220–240 VAC | 4100ES | [9 empty] | 4 Blocks | Internal |  |  | Master Controller
4100-5327 | As above; 220–240 VAC | 4100ES | [9 empty] | 4 Blocks | Internal |  |  | EPS & Accessories
4100-5401 | ES-PS: includes Aux Relay, 24 V Aux 2 A Tap/Simple NAC, 110 Ah Battery Charger, 2 PDI Blocks | 4100ES |  |  | Provides power to bay: Yes | 68 | 77 |  |  |  |  | 2 Blocks | Internal |  | See ES Power Supply Specs | Power Supplies
4100-5401 | General ES-PS/ES-XPS performance limits | 4100ES | [10 empty] | Internal | 4100-5131 | AC input 120–240 VAC; Total DC output: 9.5 A (no fan), 9.7 A (with fan & IDNAC), 12.7 A (fan w/o IDNAC); Regulated 24 V loads limit: 5.0 A; Aux power tap: 2 A max; NACs programmed for aux power: 3 A each, 5 A total; Battery charger (ES-PS only) temp-comp, dual-rate; UL/ULC listed up to 110 Ah batteries | ES PS Specs
4100-5401 | ES-PS: includes Aux Relay, 24 V Aux 2 A Tap/Simple NAC, 110 Ah Battery Charger, 2 PDI Blocks | 4100ES |  |  | Provides power to bay: Yes | 68 | 77 |  |  |  |  | 2 Blocks | Internal |  | See ES Power Supply Specs | Master Controller
4100-5401 | General ES-PS/ES-XPS performance limits | 4100ES | [10 empty] | Internal | 4100-5131 | AC input 120–240 VAC; Total DC output: 9.5 A (no fan), 9.7 A (with fan & IDNAC), 12.7 A (fan w/o IDNAC); Regulated 24 V loads limit: 5.0 A; Aux power tap: 2 A max; NACs programmed for aux power: 3 A each, 5 A total; Battery charger (ES-PS only) temp-comp, dual-rate; UL/ULC listed up to 110 Ah batteries | Master Controller
4100-5402 | ES-XPS: same as ES-PS except without battery charger | 4100ES |  |  | Provides power to bay: No | 68 | 77 |  |  |  |  | 2 Blocks | Internal |  | See ES Power Supply Specs | Master Controller
4100-5402 | General ES-PS/ES-XPS performance limits | 4100ES | [10 empty] | Internal | 4100-5131 | AC input 120–240 VAC; Total DC output: 9.5 A (no fan), 9.7 A (with fan & IDNAC), 12.7 A (fan w/o IDNAC); Regulated 24 V loads limit: 5.0 A; Aux power tap: 2 A max; NACs programmed for aux power: 3 A each, 5 A total; Battery charger (ES-PS only) temp-comp, dual-rate; UL/ULC listed up to 110 Ah batteries | Master Controller
4100-5402 | General ES-PS/ES-XPS performance limits | 4100ES | [10 empty] | Internal | 4100-5131 | AC input 120–240 VAC; Total DC output: 9.5 A (no fan), 9.7 A (with fan & IDNAC), 12.7 A (fan w/o IDNAC); Regulated 24 V loads limit: 5.0 A; Aux power tap: 2 A max; NACs programmed for aux power: 3 A each, 5 A total; Battery charger (ES-PS only) temp-comp, dual-rate; UL/ULC listed up to 110 Ah batteries | ES PS Specs
4100-5402 | ES-XPS: same as ES-PS except without battery charger | 4100ES |  |  | Provides power to bay: No | 68 | 77 |  |  |  |  | 2 Blocks | Internal |  | See ES Power Supply Specs | Power Supplies
4100-5403 | Harness for ES-PS Backup Power Supply | 4100ES | [10 empty] | Internal |  |  | Master Controller
4100-5403 | Harness for ES-PS Backup Power Supply | 4100ES | [10 empty] | Internal |  |  | PS Accessories
4100-5450 | Conventional NAC Module; 3 outputs individually selectable as NAC (Class B/A) or Aux Power | 4100ES |  |  | Three 3 A NACs (per card) | 66 | 66 |  |  |  |  | 1 Block | Internal |  | Special App: 3.0 A/NAC, 9.0 A/card; Reg 24 V: 2.0 A/NAC, 5.0 A/card | Master Controller
4100-5450 | Conventional NAC Module; 3 outputs individually selectable as NAC (Class B/A) or Aux Power | 4100ES |  |  | Three 3 A NACs (per card) | 66 | 66 |  |  |  |  | 1 Block | Internal |  | Special App: 3.0 A/NAC, 9.0 A/card; Reg 24 V: 2.0 A/NAC, 5.0 A/card | Notification Modules
4100-5451 | IDNAC Addressable Notification SLC Module | 4100ES | IDNAC |  | Three 3 A IDNAC SLCs; up to 127 addresses & 139 unit loads per SLC | 124 | 230 |  |  |  |  | 2 Blocks (on ES Power Supply only) | Internal |  | 29 VDC regulated output from ES-PS IDNAC; see wiring specs | Master Controller
4100-5451 | IDNAC Addressable Notification SLC Module | 4100ES | IDNAC |  | Three 3 A IDNAC SLCs; up to 127 addresses & 139 unit loads per SLC | 124 | 230 |  |  |  |  | 2 Blocks (on ES Power Supply only) | Internal |  | 29 VDC regulated output from ES-PS IDNAC; see wiring specs | Notification Modules
4100-6031 | City Circuit, with disconnect switches | 4100ES |  |  |  | 20 | 36 | [5 empty] | Door |  |  | Master Controller
4100-6031 | City Circuit, with disconnect switches | 4100ES |  |  |  | 20 | 36 | [5 empty] | Door |  |  | Comm-City-DACT
4100-6032 | City Circuit, without disconnect switches | 4100ES |  |  |  | 20 | 36 | [5 empty] | Door |  |  | Master Controller
4100-6032 | City Circuit, without disconnect switches | 4100ES |  |  |  | 20 | 36 | [5 empty] | Door |  |  | Comm-City-DACT
4100-6033 | Three Form C relays (Alarm, Trouble, Supervisory), 2 A resistive @ 32 VDC | 4100ES |  |  |  | 15 | 37 |  |  |  |  | 1 Block | Internal |  |  | Comm-City-DACT
4100-6033 | Three Form C relays (Alarm, Trouble, Supervisory), 2 A resistive @ 32 VDC | 4100ES |  |  |  | 15 | 37 |  |  |  |  | 1 Block | Internal |  |  | Master Controller
4100-6038 | Dual Port RS-232 with 2120 interface (slot module) | 4100ES |  |  | Max three RS-232 type modules per panel | 132 | 132 |  |  |  |  | 1 Slot | Internal |  |  | Comm-City-DACT
4100-6038 | Dual Port RS-232 with 2120 interface (slot module) | 4100ES |  |  | Max three RS-232 type modules per panel | 132 | 132 |  |  |  |  | 1 Slot | Internal |  |  | Master Controller
4100-6048 | VESDA Aspiration System Interface | 4100ES |  |  |  | 132 | 132 |  |  |  |  | 1 Slot | Internal |  |  | Comm-City-DACT
4100-6048 | VESDA Aspiration System Interface | 4100ES |  |  |  | 132 | 132 |  |  |  |  | 1 Slot | Internal |  |  | Master Controller
4100-6080 | Point or Event Reporting; includes two 2080‑9047 cables | 4100ES |  |  | Two max per system | 30 | 40 |  |  |  |  | Side mount | Internal |  |  | Master Controller
4100-6080 | Point or Event Reporting; includes two 2080‑9047 cables | 4100ES |  |  | Two max per system | 30 | 40 |  |  |  |  | Side mount | Internal |  |  | Comm-City-DACT
4100-6103 | Dual Class A IDNAC Isolator (converts one Class B IDNAC SLC to two Class A outputs; isolation on each) | 4100ES | IDNAC |  | Up to 2 per SLC (max 6 per SLC); 30 device addresses per isolated loop | 8.3 | 18.5 |  |  |  |  | 1 Block | Internal |  | Total controlled by source SLC (3 A max) | Master Controller
4100-6103 | Dual Class A IDNAC Isolator (DCAI): converts one Class B SLC to two Class A or two Class B; short circuit isolation per output | 4100ES | IDNAC |  | Up to 2 DCAIs per SLC (max 6 per EPS); each isolated output uses one IDNAC address | [7 empty] | Internal |  |  | EPS & Accessories
4100-6103 | Dual Class A IDNAC Isolator (DCAI): converts one Class B SLC to two Class A or two Class B; short circuit isolation per output | 4100ES | IDNAC |  | Up to 2 DCAIs per SLC (max 6 per EPS); each isolated output uses one IDNAC address | [7 empty] | Internal |  |  | Master Controller
4100-6103 | Dual Class A IDNAC Isolator (converts one Class B IDNAC SLC to two Class A outputs; isolation on each) | 4100ES | IDNAC |  | Up to 2 per SLC (max 6 per SLC); 30 device addresses per isolated loop | 8.3 | 18.5 |  |  |  |  | 1 Block | Internal |  | Total controlled by source SLC (3 A max) | IDNAC DCAI
4100-6311 | ESMX Loop Interface Module (dual isolated loop) | 4100ES | MX | 250 MX devices per loop | 2 MX loops; up to 250 devices/loop | 118 | 2614 |  | 2 MX loops |  | Main | 1 Block (internal) | Internal | 4100-0642 | Loop 40 VDC, per-loop 1 A max | S4100-0059
4100-6312 | ESMX Optional Loop Mezzanine (adds second loop) | 4100ES | MX | Adds +1 MX loop (250 devices) | Adds 1 loop (250 devices) |  |  |  | Adds 1 loop | 4100-6311 | Sub-module | Mezzanine on 6311 (internal) | Internal | 4100-6311 | Mounts on 4100-6311 | S4100-0059
4100-9620 | Basic Analog Audio Operation with microphone; requires dedicated expansion bay | 4100ES |  |  | Includes expansion bay, 4100-1210 analog controller board, microphone module, audio expansion bay kit | [7 empty] | Both |  |  | Master Controller
4100-9620 | Basic Analog Audio Operation with microphone; requires dedicated expansion bay | 4100ES |  |  | Includes expansion bay, 4100-1210 analog controller board, microphone module, audio expansion bay kit | [7 empty] | Both |  |  | Analog Audio (S4100-0104)
4100-9701 | ES-PS Master Controller with 2x40 Display (English); includes CPU, IDNet2 (250 pts), ES-PS w/ charger, Aux Relay & Power Tap, RUI+ | 4100ES | IDNet |  | Up to 250 IDNet points standard on ES-PS; system up to 3000 addressable points | 277 | 321 |  |  |  |  | CPU bay | Internal |  |  | Master Controller
4100-9702 | ES-PS Master Controller with 2x40 Display (Canadian French) | 4100ES |  |  | Up to 250 IDNet points standard on ES-PS; system up to 3000 addressable points | 277 | 321 |  |  |  |  | CPU bay | Internal |  |  | Master Controller
4100-9706 | ES-PS Master Controller with Color ES Touch Screen Display | 4100ES |  |  | Up to 250 IDNet points standard on ES-PS; system up to 3000 addressable points | 362 | 441 |  |  |  |  | CPU bay | Internal |  |  | Master Controller
4100-9709 | ES-PS Master Controller without local display | 4100ES |  |  | Up to 250 IDNet points standard on ES-PS; system up to 3000 addressable points | 277 | 321 |  |  |  |  | CPU bay | Internal |  |  | Master Controller
4100-9843 | Kit of 8 yellow LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-9843 | Kit of 8 yellow LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | Master Controller
4100-9844 | Kit of 8 green LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-9844 | Kit of 8 green LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | Master Controller
4100-9845 | Kit of 8 red LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | LED-Switch (4100-0032)
4100-9845 | Kit of 8 red LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | Master Controller
4100-9855 | Kit of 8 blue LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | Master Controller
4100-9855 | Kit of 8 blue LEDs | 4100ES |  |  | For 1276/1277/1300 | [7 empty] | Internal |  |  | LED-Switch (4100-0032)
IDNAC SLC | UTP required; up to 127 addresses & 139 unit loads per SLC | 4100ES | IDNAC |  | Max to any appliance: 4000 ft; Max SLC length w/ T‑taps (Class B): 10,000 ft | 0.8 mA per appliance | [6 empty] | Internal |  |  | Wiring Specs
IDNet & MAPNET (wire type) | IDNet/MAPNET (retrofit allowed) | 4100ES | IDNet |  | New: Shielded twisted pair (STP) for MAPNET / UTP for IDNet2; Retrofit: UTP allowed | [7 empty] | Internal |  |  | Wiring Specs
IDNet / MAPNET common | Max distance from control panel depends on device load count | 4100ES | IDNet |  | 1–125 devices: 4000 ft (50 Ω); 126–250: 2500 ft (35 Ω) | [7 empty] | Internal |  |  | Wiring Specs
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller
|  | 4100ES | [10 empty] | Internal |  |  | Master Controller