## Sheet1
Prompt Questions | Answer | Action Based on Answer | Action Based on Answer
Does Specs and BOQ calls for Short-Circuit isolator in each detector ? |  | If Yes -- use MX Series Devices and MX Loop Cards in Panel | if no - than-use Idnet Series Devices and Idnet Loop cards in Panels
Does Specs and BOQ calls for sof-addressable or Auto Addressing or device position based addressing in the System ? |  | If Yes -- use MX Series Devices and MX Loop Cards in Panel | if no - than-use Idnet Series Devices and Idnet Loop cards in Panels
Does Specs and BOQ calls for short-circuit isolator in each device? |  | If Yes -- use MX Series Devices and MX Loop Cards in Panel | if no - than-use Idnet Series Devices and Idnet Loop cards in Panels
Does Specs and BOQ calls for Loop Powered Sounder with no sparate Power for Sounders? |  | If Yes -- use MX Series Devices and MX Loop Cards in Panel
Does Specs and BOQ calls for all Detection and notification devices on same Loop? |  | If Yes -- use MX Series Devices and MX Loop Cards in Panel
Does specs and BOQ calls for no separate wiring for Notification devices or no separate wiring for Horns and Strobes? |  | If Yes -- use MX Series Devices and MX Loop Cards in Panel
Does BOQ mentions Speakers and specs calls for Voice Evauation System? |  | If Yes--Use 4100ES series Panel with Audio Controller and other accessories.
Does Specs mention Voice Evacuation System but No speakers in BOQ? |  | if yes - than use non-audio Panel based on device quanitities like 4007ES or 4010ES or 4100ES
Does Specs mention Speakers and Horns both and BOQ also mention Speaker and Horns? |  | If Yes--Use 4100ES series Panel with Audio Controller and other accessories.
Does Specs mention Addressable NAC circuits? |  | If yes - than use IDNAC in Panel
Does specs and/or BOQ mention addressable Notification (Horn and Strobes and/or Flashers) devices? |  | If yes - than use IDNAC in Panel
Does specs mention Panel Display to be 2x40 character LCD or bigger LCD or Touch screen LCD? |  | if yes - than use CPU with 2x40 character 4100ES panel module
Does specs and/or BOQ mention Fire Fighters Telephone? |  | if yes- than include Fire Fighters Phone Module and circuits in the 4100ES Panel
Does specs calls for Notirfication Appliance circuit to be Class A type wiring or class-B wiring? |  | if yes - than include Class -A doughter cards in the 4100ES Panel
Does Specs calls for Speaker circuits to be class A type wiring or class-B wiring? |  | if yes - than include Class -A doughter cards in the 4100ES Panel
Fire Fighter Phone Jacks shall decide fire-fighters phone circuit quantity. For every 10 jacks, there shall be one circuit.
If Audio System, does specs call for each zone wiring to be wired from two different amplifiers with alternate speakers connected to two different amplofiers such that one amplifier fauilure still provide evacuation massage to the zoen. does specs needs each zone with 2 speaker Circuits alternatively wired or single speaker circuit ? |  | if yes - than use Flex 50 or Flex-35 amplifiers in 4100ES Panels
Does specs calls for constant supervision for Speaker circuits? |  | if yes than add constant supervision mezzanine cards in 4100ES Audio Amplofiers selection
what is the wattage of Speakers mentioned in specs? |  | Calculate total Amplfier quantity needed based on this data
does specs calls for one to one Backup amplifier for Audio System ? |  | if yes - than use Flex 50 or Flex-35 amplifiers in 4100ES Panels
Does specs calls for one for all Backup amplofier for Audio system? |  | if yes - than use 100W amplifier in 4100ES Audio Panel
Does specs calls for Panel mounted Printer? |  | If yes than add RS-232 card in the Panel
Does specs calls for PC based Graphics command center with Maps and device locations identification on LCD Monitor? |  | If yes than add network cards in the Panel
Announciator type? LED or LCD? Minic Panel? |  | if LCD than select RUI card in the Panel. If LED or Mimic Panel, than separate configuration of 4100ES or RCU-SCU combination announciator needs to be configured
Smoke Management System described in Specs? How many Relays needed based on Fans qunatity? |  | If yes, than include relay cards and LED-Swicth modules in the 4100ES Panel
Network wired type or fiber? If Fiber smfo or mmfo? |  | Based on answer, select appropriate cards in the Panel
Door Holders to be 24bDC or 220VAC? |  | If 220VAC door holders, than relay cards shall be suitable for 220VAC load.
Does specs calls for Computer Graphic Command center? if yes than we select, Simplex TSW graphics - here again two ID one is economical and other one is costly. If specs calls for disable devices capability from Graphics station and/or controlling required need to go with full version software. |  | Based on answer, select appropriate Part numbers - full fledge TSW is costly. Only quote when specifically needed as per specs
Speakers with Visual or Separate Speaker and Visual |  | if speaker with Visual devices, than equal quantity of NAC circuites as per speaker circuits needs to be incoporated in the 4100ES Panel
LEDs on the Cover of the Monitor and Control Modules
Feedback Loop for Fire Dampers ? |  | if yes than Relay Cards with Feedback monitoring shall be included in the 4100ES Panel
Indication of Feedback Loop of Fire Damper on Panel using LED? |  | if yes, than LEDs shall be included in the Panel configuration of 4100ES panel
Voice Evacuation Operation Speaker circuit Selection using Switch and LEDs |  | if yes, than LED-Swicth modules shall be included in the Panel configuration of 4100ES panel
Does Remote Announciator needs to have Microphone and LED and Switches for Audio control ? |  | if yes than separate Panel with Remote Announciator Main PID shall be configured using 4100ES configurator.